EAST JOHNSON COUNTY WATER USERS ASSOCIATION, INC.

P.O. BOX 330

LAMAR, AR 72846

Instruction for Tying-On to the East Johnson County Water System

The Board of Directors of the East Johnson County Water Association, Inc. along with the State Board of Health, has set the following standards that must be met before you can be tied into the Association water system.

The Association will install the service line from the main line to the meter yoke, install the meter box, meter yoke with an 18” x ¾” threaded tail pipe, and also furnish and install the meter.

The property owner will be responsible for tying-on to the 18” x ¾” threaded tail pipe, laying the service line from the meter to the house, and connecting the pipe to the plumbing.

The property owner will be required to install on the end of the tail pipe a ¾” ball valve, a pressure reducing valve, and a dual check valve.  They should be installed with the gate valve first, followed by a short nipple, the pressure reducing valve, and the dual check valve.  Gate valves should be rated at no less than 150 psi.  Pressure reducing valves should be pre-set at between 40-50 psi.  It is recommended that all service lines be 1” PVC Sch 40 and be installed no less than 18” deep.

Prior to connecting to the Association system, the property owner must air gap their home water supply from the Association system.  The air gap must be no less than 18”.  A gate valve is not an air gap.  This is a requirement by the State Board of Health and will be inspected prior to allowing your property to be tied to into the Association system.

The Association will install meters, inspect air gaps, and turn on water by sections.  We will attempt to call customers the day prior to turn on.  If possible, we do request the property owner or a responsible person be present when we turn on the water.

The Association is requesting that you proceed to have your service line installed as indicated in the diagram below.  This needs to be completed in order to quicken the rate at which you will be able to begin receiving service.  You may go on to cover your service line, but an air gap of 18” must remain open for inspection.

Each property owner will be responsible for water leaks between the water meter and their house.

Water bills may be paid at the Association office.  Payments may also be mailed to P.O. Box 330, Lamar, AR 72846.

Installation diagram:

meter box     ball valve      pressure regulator	     dual check valve		house

The State of Arkansas Plumbing Code states:

“2.29.1.  Except as approved by the State Administrative Authority, in no case shall a residential building be allowed to connect to the same water service or building sewer of another private residential building.  Each building structure shall have separate water and/or sewer line services from the point of the utility source and in no case be interconnected with the plumbing system of another privately owned property.”